## Sheet1
1. Motor current [A]
2. Air flow [Nm3/h]
3. Discharge pressure [MPa]
4. Inlet air temp. [C]
5. IGV position [%]
6. Lub.oil pressure [Mpa]
7. Lub.oil temp. [C]
8. Vib. 2nd [micro m]
9. Vib.3rd [micro m]
10. Running hour [hr]

## Sheet2
year | 4 | 6 | dec | 6 | 6 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36 | 40 | 44 | 48 | 52 | 56 | 60 | 64 | 68 | 72 | 76 | 80 | 84 | 88 | 92 | 96 | 100 | 104 | 108 | 112 | 116 | 120 | 124 | 128 | 132 | 136 | 144 | 152 | 160 | 168 | 172 | 176 | 180 | 184 | 188 | 192 | 196 | 200 | 204 | 208 | 212 | 216 | 220 | 222 | 224 | 232 | 240
month | 2 | 10 | dec | 10 | year','month ','day','week day','hour','minute','second','comp type','operation place','IGV auto/manual','blow off open/close','comp status','loading status','ready to run','Discharge pressure (System press)','Discharge pressure (comp outlet)','Main motor current','Lube oil pressure','Reserve','reserve','Lube oil temp','reserve','final stage inlet air temp','Reserve','2nd stage shaft vib','3rd stage shaft vib','Air Flow','Reserve','Reserve','Reserve','Reserve','Reserve','Reserve','IGV position','BV position','Remote const. press. Set point','Reserve','Reserve','Reserve','Running hour','Start time','Loading hour','loading time','lube oil press. Low limit','Reserve','lube oil temp. High limit','Each stage inlet air temp high limit','each stage vib high limit','Reserve','Reserve','const press control set point','Unloading discharge press (H) set point','loading discharge press (L) set point','motor anti overload current control SP','anti-surge lower limit current','anti-surge press control SP','Reserve','aux eq status','heavy trouble','light trouble','maintain
day | 2 | 12 | dec | 12 | 6,10,12,14,16,18,20,22,24,26,28,30,32,34,36,40,44,48,52,56,60,64,68,72,76,80,84,88,92,96,100,104,108,112,116,120,124,128,132,136,144,152,160,168,172,176,180,184,188,192,196,200,204,208,212,216,220,222,224,232,240
week day | 2 | 14 | dec | 14 | 4,2,2,2,2,2,2,2,2,2,2,2,2,2,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,4,8,8,8,8,4,4,4,4,4,4,4,4,4,4,4,4,4,2,2,8,8,8
hour | 2 | 16 | dec | 16 | dec','dec','dec','dec','dec','dec','dec','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex','hex
minute | 2 | 18 | dec | 18 | year','month ','day','week day','hour','minute','second','comp type','operation place','IGV auto/manual','blow off open/close','comp status','loading status','ready to run','Discharge pressure (System press)','Discharge pressure (comp outlet)','Main motor current','Lube oil pressure','Reserve','reserve','Lube oil temp','reserve','final stage inlet air temp','Reserve','2nd stage shaft vib','3rd stage shaft vib','Air Flow','Reserve','Reserve','Reserve','Reserve','Reserve','Reserve','IGV position','BV position','Remote const. press. Set point','Reserve','Reserve','Reserve','Running hour','Start time','Loading hour','loading time','lube oil press. Low limit','Reserve','lube oil temp. High limit','Each stage inlet air temp high limit','each stage vib high limit','Reserve','Reserve','const press control set point','Unloading discharge press (H) set point','loading discharge press (L) set point','motor anti overload current control SP','anti-surge lower limit current','anti-surge press control SP','Reserve','aux eq status','heavy trouble','light trouble','maintain
second | 2 | 20 | dec | 20
comp type | 2 | 22 | hex | 22
operation place | 2 | 24 | hex | 24
IGV auto/manual | 2 | 26 | hex | 26
blow off open/close | 2 | 28 | hex | 28
comp status | 2 | 30 | hex | 30
loading status | 2 | 32 | hex | 32
ready to run | 2 | 34 | hex | 34
Discharge pressure (System press) | 4 | 36 | hex | 36
Discharge pressure (comp outlet) | 4 | 40 | hex | 40
Main motor current | 4 | 44 | hex | 44
Lube oil pressure | 4 | 48 | hex | 48
Reserve | 4 | 52 | hex | 52
reserve | 4 | 56 | hex | 56
Lube oil temp | 4 | 60 | hex | 60
reserve | 4 | 64 | hex | 64
final stage inlet air temp | 4 | 68 | hex | 68
Reserve | 4 | 72 | hex | 72
2nd stage shaft vib | 4 | 76 | hex | 76
3rd stage shaft vib | 4 | 80 | hex | 80
Air Flow | 4 | 84 | hex | 84
Reserve | 4 | 88 | hex | 88
Reserve | 4 | 92 | hex | 92
Reserve | 4 | 96 | hex | 96
Reserve | 4 | 100 | hex | 100
Reserve | 4 | 104 | hex | 104
Reserve | 4 | 108 | hex | 108
IGV position | 4 | 112 | hex | 112
BV position | 4 | 116 | hex | 116
Remote const. press. Set point | 4 | 120 | hex | 120
Reserve | 4 | 124 | hex | 124
Reserve | 4 | 128 | hex | 128
Reserve | 4 | 132 | hex | 132
Running hour | 8 | 136 | hex | 136
Start time | 8 | 144 | hex | 144
Loading hour | 8 | 152 | hex | 152
loading time | 8 | 160 | hex | 160
lube oil press. Low limit | 4 | 168 | hex | 168
Reserve | 4 | 172 | hex | 172
lube oil temp. High limit | 4 | 176 | hex | 176
Each stage inlet air temp high limit | 4 | 180 | hex | 180
each stage vib high limit | 4 | 184 | hex | 184
Reserve | 4 | 188 | hex | 188
Reserve | 4 | 192 | hex | 192
const press control set point | 4 | 196 | hex | 196
Unloading discharge press (H) set point | 4 | 200 | hex | 200
loading discharge press (L) set point | 4 | 204 | hex | 204
motor anti overload current control SP | 4 | 208 | hex | 208
anti-surge lower limit current | 4 | 212 | hex | 212
anti-surge press control SP | 4 | 216 | hex | 216
Reserve | 2 | 220 | hex | 220
aux eq status | 2 | 222 | hex | 222
heavy trouble | 8 | 224 | hex | 224
light trouble | 8 | 232 | hex | 232
maintain | 8 | 240 | hex | 240

## Register list
Item | Data Type | Unit | Address
year | Integer |  | 40001
month | Integer |  | 40002
day | Integer |  | 40003
week day | Integer |  | 40004
hour | Integer |  | 40005
minute | Integer |  | 40006
second | Integer |  | 40007
comp type | Integer |  | 40008
operation place | Integer |  | 40009
IGV auto/manual | Integer |  | 40010
blow off open/close | Integer |  | 40011
comp status | Integer |  | 40012
loading status | Integer |  | 40013
ready to run | Integer |  | 40014
Discharge pressure (System press) | Integer | kPa | 40015
Discharge pressure (comp outlet) | Integer | kPa | 40016
Main motor current | Integer | 0.1A | 40017
Lube oil pressure | Integer | kPa | 40018
Reserve | Integer |  | 40019
reserve | Integer |  | 40020
Lube oil temp | Integer | 0.1°C | 40021
reserve | Integer |  | 40022
final stage inlet air temp | Integer | 0.1°C | 40023
Reserve | Integer |  | 40024
2nd stage shaft vib | Integer | 0.1μm | 40025
3rd stage shaft vib | Integer | 0.1μm | 40026
Air Flow | Integer | Nm³/h | 40027
Reserve | Integer |  | 40028
Reserve | Integer |  | 40029
Reserve | Integer |  | 40030
Reserve | Integer |  | 40031
Reserve | Integer |  | 40032
Reserve | Integer |  | 40033
IGV position | Integer | 0.1% | 40034
BV position | Integer | 0.1% | 40035
Remote const. press. Set point | Integer | kPa | 40036
Reserve | Integer |  | 40037
Reserve | Integer |  | 40038
Reserve | Integer |  | 40039
Running hour | Integer | Hr | 40040
Start time | Integer | Time | 40041
Loading hour | Integer | Hr | 40042
loading time | Integer | Time | 40043
lube oil press. Low limit | Integer | kPa | 40044
Reserve | Integer |  | 40045
lube oil temp. High limit | Integer | 0.1°C | 40046
Each stage inlet air temp high limit | Integer | 0.1°C | 40047
each stage vib high limit | Integer | 0.1μm | 40048
Reserve | Integer |  | 40049
Reserve | Integer |  | 40050
const press control set point | Integer | kPa | 40051
Unloading discharge press (H) set point | Integer | kPa | 40052
loading discharge press (L) set point | Integer | kPa | 40053
motor anti overload current control SP | Integer | 0.1A | 40054
anti-surge lower limit current | Integer | 0.1A | 40055
anti-surge press control SP | Integer | kPa | 40056
Reserve | Integer |  | 40057
aux eq status | Integer |  | 40058
heavy trouble | Integer |  | 40059
light trouble | Integer |  | 40060
maintain | Integer |  | 40061